## Fault Mapping
Equipment location | FD Platform Fault Name | Fault Mapping to FSBrick
AHU3 | Heating Valve Stuck Closed | Valve_Stuck (brick:Heating_Water_Valve)
AHU9 | Cooling Valve Leaking | Valve_Leakage (brick:Cooling_Valve)
AHU2 | Exhaust Air Damper is Open But No Airflow | Damper_Malfunctioning (brick:Exhaust_Damper)

## Fault Severity Mapping
Equipment location | FD Platform Fault Name | Fault Severity Mapping to FSBrick
AHU3 | Heating Valve Stuck Closed | hasSeverity; brick:Position with value Literal
AHU9 | Cooling Valve Leaking |  | **No specified severity
AHU2 | Exhaust Air Damper is Open But No Airflow |  | **No specified severity

## Symptom Mapping
Equipment location | Threshold-Based Alarm Name | Symptom Mapping | BAS Symptom Element Entity | Symptom Element Mapping
AHU3 | ¦OA Airflow - OA Airflow Min Setpoint¦ < 200 cfm (TRUE for no alarm) | brick:Air_Flow_Alarm (brick:Outside_Air) | OA Airflow | brick:Air_Flow_Sensor
|  |  | OA Airflow Min Setpoint | brick:Min_Air_Flow_Setpoint_Limit
| OA damper position feedback -OA Damper Min Position Setpoint > 0 (TRUE for no alarm) | brick:*Damper_Position_Alarm (brick:Outside_Damper) | OA Damper Position Feedback | brick:Damper_Position_Sensor
|  |  | OA Damper Min Postion Setpoint | brick:Min_Position_Setpoint_Limit
| ¦PHT Supply Temperature - PHT Supply Temperature Setpoint¦ < 2.5 (TRUE for no alarm) (PHT = preheat valve) | brick:Water_Temperature_Alarm (brick:Preheat_Hot_Water_System) | PHT Supply Temperature | brick:Water_Temperature_Sensor
|  |  | PHT Supply Temperature Setpoint | brick:Water_Temperature_Setpoint
AHU9 | ¦OA Airflow - OA Airflow Min Setpoint¦ < 200 cfm (TRUE for no alarm) | brick:Air_Flow_Alarm (brick:Outside_Air) | OA Airflow | brick:Air_Flow_Sensor
|  |  | OA Airflow Min Setpoint | brick:Min_Air_Flow_Setpoint_Limit
| OA damper position feedback -OA Damper Min Position Setpoint > 0 (TRUE for no alarm) | brick:*Damper_Position_Alarm (brick:Outside_Damper) | OA Damper Position Feedback | brick:Damper_Position_Sensor
|  |  | OA Damper Min Postion Setpoint | brick:Min_Position_Setpoint_Limit
| ¦PHT Supply Temperature - PHT Supply Temperature Setpoint¦ < 2.5 (TRUE for no alarm) (PHT = preheat valve) | brick:Water_Temperature_Alarm (brick:Preheat_Hot_Water_System) | PHT Supply Temperature | brick:Water_Temperature_Sensor
|  |  | PHT Supply Temperature Setpoint | brick:Water_Temperature_Setpoint
| ¦SA Static Pressure Actual - SA Static Pressure Setpoint¦ < 0.5 (TRUE for no alarm) | brick:Pressure_Alarm (brick:Supply_Air) | SA Static Pressure Actual | brick:Static_Pressure_Sensor
|  |  | SA Static Pressure Setpoint | brick:Static_Pressure_Setpoint
| ¦SA Temperature Actual - SA Temperature Setpoint¦ < 2.5 (TRUE for no alarm) | brick:Air_Temperature_Alarm (brick:Supply_Air) | SA Temperature Actual | brick:Air_Temperature_Sensor
|  |  | SA Temperature Setpoint | brick:Air_Temperature_Setpoint
AHU2 | ¦OA Airflow - OA Airflow Min Setpoint¦ < 200 cfm (TRUE for no alarm) | brick:Air_Flow_Alarm (brick:Outside_Air) | OA Airflow | brick:Air_Flow_Sensor
|  |  | OA Airflow Min Setpoint | brick:Min_Air_Flow_Setpoint_Limit
| ¦PHT Supply Temperature - PHT Supply Temperature Setpoint¦ < 2.5 (TRUE for no alarm) (PHT = preheat valve) | brick:Water_Temperature_Alarm (brick:Preheat_Hot_Water_System) | PHT Supply Temperature | brick:Water_Temperature_Sensor
|  |  | PHT Supply Temperature Setpoint | brick:Water_Temperature_Setpoint